## GHPH-MM3xx
Technical Specification Sheet for Heat Pump Space Heater - Three Phase
Product Brief | Unit | Parameter | Parameter | Parameter
Brand |  | Grundig | Grundig | Grundig
Model No. |  | GHPH-MM312 | GHPH-MM314 | GHPH-MM316
Stock Code |  | 8509473600 | 8509483600 | 8509493600
EAN Code |  | 4013833067412 | 4013833067429 | 4013833067436
Power Supply
Rated Power | W | 14700 | 15100 | 15500
Voltage/Frequency/Phase | V/Hz | 380-415V~ / 50Hz / 3 Phase | 380-415V~ / 50Hz / 3 Phase | 380-415V~ / 50Hz / 3 Phase
Power Supply Voltage Option |  | N/A | N/A | N/A
Plug Type |  | NO NEED | NO NEED | NO NEED
Power Plug |  | N/A | N/A | N/A
Power Supply Cord | mm2 | 5*10mm2 | 5*10mm2 | 5*10mm2
Wired Controller |  | YES | YES | YES
Electric Heater |  | JGS03-230V 9000W 13.6A | JGS03-230V 9000W 13.6A | JGS03-230V 9000W 13.6A
Thermostat on Electric Heater |  | BW-S 70℃ | BW-S 70℃ | BW-S 70℃
Features & Accessories
Main Features
Refrigerant |  | R32 | R32 | R32
Total Refrigerant Amount (g) | g | 1750 | 2100 | 2100
GWP |  | 675 | 675 | 675
CO2 equivalent | Ton | 1.1812 | 1.417 | 1.417
Protection against electric shock (Class I, II, III) |  | Class I | Class I | Class I
Climate Class |  | T1 | T1 | T1
Heating Type |  | Heat Pump | Heat Pump | Heat Pump
Power Supply Connection |  | - | - | -
Recommended Circuit Breaker | A | 50 | 50 | 50
Flow control of refrigerant |  | Electronic expansion valve | Electronic expansion valve | Electronic expansion valve
Product Definition
Filters |  | NO | NO | NO
Extra Filters |  | NO | NO | NO
Remote Control |  | Wired Controller, LCD | Wired Controller, LCD | Wired Controller, LCD
Digital_Display |  | LCD | LCD | LCD
Jet Cool |  | N/A | N/A | N/A
Jet Heat |  | N/A | N/A | N/A
Auto Restart Function |  | YES | YES | YES
Dehumidifying Function |  | N/A | N/A | N/A
Automatic Temperature Control |  | YES | YES | YES
Timer Function |  | 0.5~24H | 0.5~24H | 0.5~24H
Defrost Function |  | YES | YES | YES
Hotstart |  | YES | YES | YES
Energy Saving Mode(Fuzzy) |  | YES (ECO) | YES (ECO) | YES (ECO)
WIFI Control |  | YES | YES | YES
APP Function |  | YES, HomeDirect | YES, HomeDirect | YES, HomeDirect
Other Function |  | SG Ready, Climate Related Curves, Two Zones Control, Solar Energy, Auxiliary Heat Source, Cascade | SG Ready, Climate Related Curves, Two Zones Control, Solar Energy, Auxiliary Heat Source, Cascade | SG Ready, Climate Related Curves, Two Zones Control, Solar Energy, Auxiliary Heat Source, Cascade
Main Performance
Cooling Capacity - PdesignC at 7⁰C Water Outlet | kW | 11.4 | 13.5 | 15.5
SEER at at 7⁰C Water Outlet | W/W | 4.8 | 4.5 | 4.21
Warmer Climate
Heating Capacity - PdesignH at 35⁰C Water Outlet under Warmer Climate Condition | kW | 12.2 | 14 | 15.7
SCOP at 35⁰C Water Outlet under Warmer Climate Condition | W/W | 6.6 | 6.2 | 6
Seasonal space heating energy efficiency at 35⁰C Water Outlet under Warmer Climate Condition |  | 261% | 253% | 240%
The Annual Energy Consumption at 35⁰C Water Outlet under Warmer Climate Condition | kW/h | 2489 | 3036 | 3515
Heating Capacity - PdesignH at 55⁰C Water Outlet under Warmer Climate Condition | kW | 12 | 13.5 | 15.2
SCOP at 55⁰C Water Outlet under Warmer Climate Condition | W/W | 4.5 | 4.1 | 4.2
Seasonal space heating energy efficiency at 55⁰C Water Outlet under Warmer Climate Condition |  | 177% | 161% | 165%
The Annual Energy Consumption at 55⁰C Water Outlet under Warmer Climate Condition | kW/h | 3582 | 4419 | 4855
Average Climate
Heating Capacity - PdesignH at 35⁰C Water Outlet under Average Climate Condition | kW | 11.5 | 13.2 | 15
SCOP at 35⁰C Water Outlet under Average Climate Condition | W/W | 4.5 | 4.5 | 4.4
Seasonal space heating energy efficiency at 35⁰C Water Outlet under Average Climate Condition |  | 177% | 177% | 173%
The Annual Energy Consumption at 35⁰C Water Outlet under Average Climate Condition | kW/h | 6066 | 6960 | 8085
Heating Capacity - PdesignH at 55⁰C Water Outlet under Average Climate Condition | kW | 10.8 | 12.4 | 12.8
SCOP at 55⁰C Water Outlet under Average Climate Condition | W/W | 3.3 | 3.3 | 3.3
Seasonal space heating energy efficiency at 55⁰C Water Outlet under Average Climate Condition |  | 130% | 130% | 130%
The Annual Energy Consumption at 55⁰C Water Outlet under Average Climate Condition | kW/h | 7763 | 8910 | 9197
Colder Climate
Heating Capacity - PdesignH at 35⁰C Water Outlet under Colder Climate Condition | kW | 10.3 | 12.1 | 13.8
SCOP at 35⁰C Water Outlet under Colder Climate Condition | W/W | 4 | 3.8 | 3.7
Seasonal space heating energy efficiency at 35⁰C Water Outlet under Colder Climate Condition |  | 157% | 150% | 145%
The Annual Energy Consumption at 35⁰C Water Outlet under Colder Climate Condition | kW/h | 6347 | 7869 | 9213
Heating Capacity - PdesignH at 55⁰C Water Outlet under Colder Climate Condition | kW | 9.8 | 10.5 | 11.6
SCOP at 55⁰C Water Outlet under Colder Climate Condition | W/W | 3 | 2.9 | 3
Seasonal space heating energy efficiency at 55⁰C Water Outlet under Colder Climate Condition |  | 116% | 114% | 116%
The Annual Energy Consumption at 55⁰C Water Outlet under Colder Climate Condition | kW/h | 8072 | 8945 | 9551
Energy Level - at 35⁰C Water Outlet - (According (EU) No 811/2013 Table 2) |  | A+++ | A+++ | A+++
Energy Level - at 55⁰C Water Outlet - (According (EU) No 811/2013 Table 1) |  | A++ | A++ | A++
Maximum Cooling Power Input | W | 5500 | 5900 | 6800
Maximum Cooling Current | A | 8 | 8.6 | 9.9
Maximum Heating Power Input | W | 14700 | 15100 | 15500
Maximum Heating Current | A | 21.5 | 22 | 22.5
Noise Power Level - Outdoor Unit (Sound Power) | dBA | 64 | 65 | 68
Noise Pressure Level - Outdoor Unit (Sound Pressure) | dBA | 52 | 53.5 | 52.9
Rated Power Input - EN 60335 | W | 14700 | 15100 | 15500
Rated Current Input - EN 60335 | A | 21.5 | 22 | 22.5
Max Allowable Pressure | Mpa | 4.5 | 4.5 | 4.5
Suction Pressure Range | Mpa | 2.6 | 2.6 | 2.6
Discharge Pressure Range | Mpa | 4.5 | 4.5 | 4.5
Rated Water Flow | m3/h | 2.06 | 2.41 | 2.75
Rated Water Pressure | Mpa | 0.3 | 0.3 | 0.3
Maximum Water Pressure | Mpa | 1 | 1 | 1
Locked Motor Current (L.R.A.) | A | N/A | N/A | N/A
Working temperature range Cooling | ⁰C | 5~48 | 5~48 | 5~48
Working temperature range Heating | ⁰C | -25~35 | -25~35 | -25~35
Working temperature range DWH | ⁰C | -25~43 | -25~43 | -25~43
Water outlet temperature range Cooling | ⁰C | 7~25 | 7~25 | 7~25
Water outlet temperature range Heating | ⁰C | 25~65 | 25~65 | 25~65
Water outlet temperature range DWH | ⁰C | 25~55 | 25~55 | 25~55
Accessories
Remote Control Battery |  | / | / | /
Y-shape filter |  | YES | YES | YES
Wired Controller |  | YES | YES | YES
Connection cable of Wired Controller |  | YES | YES | YES
Length of Connection cable of Wired Controller | m | 20 | 20 | 20
Water Temperature Sensor |  | YES | YES | YES
Length of Water Temperature Sensor | m | 8 | 8 | 8
Drian hose |  | YES | YES | YES
Tighten belt |  | YES | YES | YES
Network matching wires |  | YES | YES | YES
Other Accessories |  | Anti-vibration rubber foot + IOM manual | Anti-vibration rubber foot + IOM manual | Anti-vibration rubber foot + IOM manual
Logistics Info
Product Net Dimension (WxHxD) (mm) | mm | 1135x803x396 | 1203x860x436 | 1203x860x436
Product Net Weight (kg) | kg | 115 | 140 | 140
Packed Dimension (WxHxD) (mm) | mm | 1260x982x488 | 1285x1040x495 | 1285x1040x495
Gross Weight (kg) | kg | 132 | 159 | 159
WEEE Weight (kg) | kg | 115 | 140 | 140
20' Container | pcs. | 40 | 38 | 38
40' GP Container | pcs. | 84 | 82 | 82
40' HQ Container | pcs. | 84 | 82 | 82

## GHPH-MMxx
Technical Specification Sheet for Heat Pump Space Heater - Single Phase
Product Brief | Unit | Parameter | Parameter | Parameter | Parameter | Parameter
Brand |  | Grundig | Grundig | Grundig | Grundig | Grundig
Model No. |  | GHPH-MM08 | GHPH-MM10 | GHPH-MM12 | GHPH-MM14 | GHPH-MM16
Stock Code |  | 8509423600 | 8509433600 | 8509443600 | 8509453600 | 8509463600
EAN Code |  | 4013833067368 | 4013833067375 | 4013833067382 | 4013833067399 | 4013833067405
Power Supply
Rated Power | W | 6800 | 7500 | 8700 | 9100 | 9500
Voltage/Frequency/Phase | V/Hz | 220-240V~ / 50 Hz / 1 Phase | 220-240V~ / 50 Hz / 1 Phase | 220-240V~ / 50 Hz / 1 Phase | 220-240V~ / 50 Hz / 1 Phase | 220-240V~ / 50 Hz / 1 Phase
Power Supply Voltage Option |  | N/A | N/A | N/A | N/A | N/A
Plug Type |  | NO NEED | NO NEED | NO NEED | NO NEED | NO NEED
Power Plug |  | N/A | N/A | N/A | N/A | N/A
Power Supply Cord | mm2 | 3*10mm2 | 3*10mm2 | 3*10mm2 | 3*10mm2 | 3*10mm2
Wired Controller |  | GR-LC10 (invest controller) | GR-LC10 (invest controller) | GR-LC10 (invest controller) | GR-LC10 (invest controller) | GR-LC10 (invest controller)
Electric Heater |  | JGS 220V 3000W,13.6A | JGS 220V 3000W,13.6A | JGS 220V 3000W,13.6A | JGS 220V 3000W,13.6A | JGS 220V 3000W,13.6A
Thermostat on Electric Heater |  | BW-S 70℃ | BW-S 70℃ | BW-S 70℃ | BW-S 70℃ | BW-S 70℃
Features & Accessories
Main Features
Refrigerant |  | R32 | R32 | R32 | R32 | R32
Total Refrigerant Amount (g) | g | 1300 | 1500 | 1750 | 2100 | 2100
GWP |  | 675 | 675 | 675 | 675 | 675
CO2 equivalent | Ton | 0.8775 | 1.0125 | 1.1812 | 1.417 | 1.417
Protection against electric shock (Class I, II, III) |  | Class I | Class I | Class I | Class I | Class I
Climate Class |  | T1 | T1 | T1 | T1 | T1
Heating Type |  | Heat Pump | Heat Pump | Heat Pump | Heat Pump | Heat Pump
Power Supply Connection |  | - | - | - | - | -
Recommended Circuit Breaker | A | 40 | 40 | 50 | 50 | 50
Flow control of refrigerant |  | Electronic expansion valve | Electronic expansion valve | Electronic expansion valve | Electronic expansion valve | Electronic expansion valve
Product Definition
Filters |  | NO | NO | NO | NO | NO
Extra Filters |  | NO | NO | NO | NO | NO
Remote Control |  | Wired Controller, LCD | Wired Controller, LCD | Wired Controller, LCD | Wired Controller, LCD | Wired Controller, LCD
Digital_Display |  | LCD | LCD | LCD | LCD | LCD
Jet Cool |  | N/A | N/A | N/A | N/A | N/A
Jet Heat |  | N/A | N/A | N/A | N/A | N/A
Auto Restart Function |  | YES | YES | YES | YES | YES
Dehumidifying Function |  | N/A | N/A | N/A | N/A | N/A
Automatic Temperature Control |  | YES | YES | YES | YES | YES
Timer Function |  | 0.5~24H | 0.5~24H | 0.5~24H | 0.5~24H | 0.5~24H
Defrost Function |  | YES | YES | YES | YES | YES
Hotstart |  | YES | YES | YES | YES | YES
Energy Saving Mode(Fuzzy) |  | YES (ECO) | YES (ECO) | YES (ECO) | YES (ECO) | YES (ECO)
WIFI Control |  | YES | YES | YES | YES | YES
APP Function |  | YES, HomeDirect | YES, HomeDirect | YES, HomeDirect | YES, HomeDirect | YES, HomeDirect
Other Function |  | SG Ready, Climate Related Curves, Two Zones Control, Solar Energy, Auxiliary Heat Source, Cascade | SG Ready, Climate Related Curves, Two Zones Control, Solar Energy, Auxiliary Heat Source, Cascade | SG Ready, Climate Related Curves, Two Zones Control, Solar Energy, Auxiliary Heat Source, Cascade | SG Ready, Climate Related Curves, Two Zones Control, Solar Energy, Auxiliary Heat Source, Cascade | SG Ready, Climate Related Curves, Two Zones Control, Solar Energy, Auxiliary Heat Source, Cascade
Main Performance
Cooling Capacity - PdesignC at 7⁰C Water Outlet | kW | 7.6 | 9.4 | 11.4 | 13.5 | 15.5
SEER at at 7⁰C Water Outlet | W/W | 4.5 | 4.5 | 4.8 | 4.5 | 4.21
Warmer Climate
Heating Capacity - PdesignH at 35⁰C Water Outlet under Warmer Climate Condition | kW | 8.1 | 10 | 12.2 | 14 | 15.7
SCOP at 35⁰C Water Outlet under Warmer Climate Condition | W/W | 5.8 | 5.3 | 6.6 | 6.2 | 6
Seasonal space heating energy efficiency at 35⁰C Water Outlet under Warmer Climate Condition |  | 231% | 212% | 261% | 253% | 240%
The Annual Energy Consumption at 35⁰C Water Outlet under Warmer Climate Condition | kW/h | 1885 | 2541 | 2489 | 3036 | 3515
Heating Capacity - PdesignH at 55⁰C Water Outlet under Warmer Climate Condition | kW | 8 | 9.9 | 12 | 13.5 | 15.2
SCOP at 55⁰C Water Outlet under Warmer Climate Condition | W/W | 4.2 | 4.6 | 4.5 | 4.1 | 4.2
Seasonal space heating energy efficiency at 55⁰C Water Outlet under Warmer Climate Condition |  | 165% | 182% | 177% | 161% | 165%
The Annual Energy Consumption at 55⁰C Water Outlet under Warmer Climate Condition | kW/h | 2565 | 2895 | 3582 | 4419 | 4855
Average Climate
Heating Capacity - PdesignH at 35⁰C Water Outlet under Average Climate Condition | kW | 7.6 | 8.7 | 11.5 | 13.2 | 15
SCOP at 35⁰C Water Outlet under Average Climate Condition | W/W | 4.5 | 4.5 | 4.5 | 4.5 | 4.4
Seasonal space heating energy efficiency at 35⁰C Water Outlet under Average Climate Condition |  | 180% | 180% | 180% | 175% | 175%
The Annual Energy Consumption at 35⁰C Water Outlet under Average Climate Condition | kW/h | 3489.2444 | 4132 | 5280 | 6198 | 7043
Heating Capacity - PdesignH at 55⁰C Water Outlet under Average Climate Condition | kW | 6.6 | 7.3 | 10.8 | 12.6 | 14
SCOP at 55⁰C Water Outlet under Average Climate Condition | W/W | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
Seasonal space heating energy efficiency at 55⁰C Water Outlet under Average Climate Condition |  | 130% | 132% | 132% | 132% | 132%
The Annual Energy Consumption at 55⁰C Water Outlet under Average Climate Condition | kW/h | 4069 | 4695 | 6761 | 7826 | 8765
Colder Climate
Heating Capacity - PdesignH at 35⁰C Water Outlet under Colder Climate Condition | kW | 6.4 | 7.6 | 10.3 | 12.1 | 13.8
SCOP at 35⁰C Water Outlet under Colder Climate Condition | W/W | 3.8 | 4 | 4 | 3.8 | 3.7
Seasonal space heating energy efficiency at 35⁰C Water Outlet under Colder Climate Condition |  | 152% | 160% | 157% | 150% | 145%
The Annual Energy Consumption at 35⁰C Water Outlet under Colder Climate Condition | kW/h | 4246.5789 | 4778.5 | 6347 | 7869 | 9213
Heating Capacity - PdesignH at 55⁰C Water Outlet under Colder Climate Condition | kW | 5.4 | 6.6 | 9.8 | 10.5 | 11.6
SCOP at 55⁰C Water Outlet under Colder Climate Condition | W/W | 2.5 | 2.7 | 3 | 2.9 | 3
Seasonal space heating energy efficiency at 55⁰C Water Outlet under Colder Climate Condition |  | 99% | 108% | 116% | 114% | 116%
The Annual Energy Consumption at 55⁰C Water Outlet under Colder Climate Condition | kW/h | 5419.4 | 6120.5556 | 8072 | 8945 | 9551
Energy Level - at 35⁰C Water Outlet - (According (EU) No 811/2013 Table 2) |  | A+++ | A+++ | A+++ | A+++ | A+++
Energy Level - at 55⁰C Water Outlet - (According (EU) No 811/2013 Table 1) |  | A++ | A++ | A++ | A++ | A++
Maximum Cooling Power Input | W | 3700 | 4300 | 5500 | 5900 | 6800
Maximum Cooling Current | A | 16.1 | 18.7 | 23.9 | 25.6 | 29.5
Maximum Heating Power Input | W | 6800 | 7500 | 8700 | 9100 | 9500
Maximum Heating Current | A | 29.5 | 32.6 | 37.8 | 39.6 | 41.3
Noise Power Level - Outdoor Unit (Sound Power) | dBA | 59 | 60 | 64 | 65 | 68
Noise Pressure Level - Outdoor Unit (Sound Pressure) | dBA | 48 | 49 | 52 | 53.5 | 52.9
Rated Power Input - EN 60335 | W | 6800 | 7500 | 8700 | 9100 | 9500
Rated Current Input - EN 60335 | A | 29.5 | 32.6 | 37.8 | 39.6 | 41.3
Max Allowable Pressure | Mpa | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Suction Pressure Range | Mpa | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
Discharge Pressure Range | Mpa | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Rated Water Flow | m3/h | 1.38 | 1.72 | 2.06 | 2.41 | 2.75
Rated Water Pressure | Mpa | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Maximum Water Pressure | Mpa | 1 | 1 | 1 | 1 | 1
Locked Motor Current (L.R.A.) | A | N/A | N/A | N/A | N/A | N/A
Working temperature range Cooling | ⁰C | 5~48 | 5~48 | 5~48 | 5~48 | 5~48
Working temperature range Heating | ⁰C | -25~35 | -25~35 | -25~35 | -25~35 | -25~35
Working temperature range DWH | ⁰C | -25~43 | -25~43 | -25~43 | -25~43 | -25~43
Water outlet temperature range Cooling | ⁰C | 7~25 | 7~25 | 7~25 | 7~25 | 7~25
Water outlet temperature range Heating | ⁰C | 25~65 | 25~65 | 25~65 | 25~65 | 25~65
Water outlet temperature range DWH | ⁰C | 25~55 | 25~55 | 25~55 | 25~55 | 25~55
Accessories
Remote Control Battery |  | / | / | / | / | /
Y-shape filter |  | YES | YES | YES | YES | YES
Wired Controller |  | YES | YES | YES | YES | YES
Connection cable of Wired Controller |  | YES | YES | YES | YES | YES
Length of Connection cable of Wired Controller | m | 20 | 20 | 20 | 20 | 20
Water Temperature Sensor |  | YES | YES | YES | YES | YES
Length of Water Temperature Sensor | m | 8 | 8 | 8 | 8 | 8
Drian hose |  | YES | YES | YES | YES | YES
Tighten belt |  | YES | YES | YES | YES | YES
Network matching wires |  | YES | YES | YES | YES | YES
Other Accessories |  | Anti-vibration rubber foot + IOM manual | Anti-vibration rubber foot + IOM manual | Anti-vibration rubber foot + IOM manual | Anti-vibration rubber foot + IOM manual | Anti-vibration rubber foot + IOM manual
Logistics Info
Product Net Dimension (WxHxD) (mm) | mm | 1125×703×370 | 1135×803×396 | 1135×803×396 | 1203×860×436 | 1203×860×436
Product Net Weight (kg) | kg | 82.5 | 99 | 103 | 126 | 126
Packed Dimension (WxHxD) (mm) | mm | 1200×865×425 | 1260×982×488 | 1260×982×488 | 1305×1040×495 | 1305×1040×495
Gross Weight (kg) | kg | 96 | 114 | 123 | 145 | 145
WEEE Weight (kg) | kg | 82.5 | 99 | 103 | 126 | 126
20' Container | pcs. | 42 | 40 | 40 | 38 | 38
40' GP Container | pcs. | 88 | 84 | 84 | 82 | 82
40' HQ Container | pcs. | 132 | 84 | 84 | 82 | 82